	BBRI
[image: image11.png]



CSTC-WTCB
	Belgian Building Research Institute
Institution RECOGNISED by application of the decree-law of 30 january 1947

	-
Test centre : B-1342 Limelette, avenue P. Holoffe, 21
Tel : (32) 2 655 77 11
Fax : (32) 2 653 07 29

-
Offices : B-1932 Sint-Stevens-Woluwe, Lozenberg, 7
Tel : (32) 2 716 42 11
Fax : (32) 2 725 32 12

-
Head office : B-1060 Brussels, Boulevard Poincaré, 79
Tel : (32) 2 502 66 90
Fax : (32) 2 502 81 80

VAT n° : BE 407.695.057


Page 1/13

	LABORATORY : 

Technology of building services
	TEST REPORT
	N° DE
:
	661 X 215 

	
	
	N° Labo
:
	TE 04.003

	
	
	N° Sample
:
	See §2

	REQUESTED BY :
STUDOR Limited, 23 Old Steine, Brighton BN1 1EL UK

	Contact persons :
- Demander -
- BBRI -
Steven White
K. De Cuyper


	Test carried out :
drop test, initial tightness, tightness after endurance, air capacity, opening pressure and effectiveness at temperatures below zero of STUDOR MINI-VENT air admittance valves for drainage systems

	References :


EN 12380 : Air admittance valves for drainage systems –Requirements, tests methods and evaluation of conformity. (version December 2002)



	Date and reference of the request
:
2004.08.31
Date of receipt of the sample(s)
:
2004.08.27
Test date
:
between 2004.09.20 and 2004.10.05
Drafting date of the report
:
2004.10.27

	This report contains 13 pages, numbered from  1/ 13 to 13/13; it may only be reproduced in its entirety.

Each page of the original report has been stamped (in red) by the laboratory and initialled by the head of laboratory. The results and findings are only valid for the tested samples.


Sample(s) to be removed from our laboratories 60 calendar days after sending of the report, unless a written request is received by the demander of the test.

	
In charge of the test :

Technical assistance  : P. Despeer
	The Head of Laboratory

K. De Cuyper, Ir


1. Introduction:

The purpose of the testing was to verify whether “STUDOR MINI-VENT” air admittance valves, indicated hereafter as “AAV”, fulfill the requirements of the European standard EN 12380 for class AI valves.

2. Samples

Ten visually identical AAV were received by BBRI Limelette on 2004.08.27, all equipped with a beige connector for assembling them on different pipes. All were packed in an octagonal insulating box. Besides marks referring to different approval systems, the valves are marked as follows:  

          MADE IN USA

STUDOR®
MINI-VENT™
[image: image1.wmf]
DN 50  A1   EN 12380

The photos 1 to 9 describe the concerned valves.

They received the following sample numbers: 2004/36/003- 1 till 10.


3. Testing

3.1.  Drop test of the AAV

The samples 1,2,3,4,5,6 and 7 were submitted to the drop test:

Results:

	AAV

sample N° 2004/36/003-
	Date of testing
	Orientation
	Pass the test

	
	
	1
	2
	3
	

	1
	2004.09.20
	OK
	OK
	OK
	Yes

	2
	2004.09.20
	OK
	OK
	OK
	Yes

	3
	2004.09.20
	OK
	OK
	OK
	Yes

	4
	2004.09.20
	OK
	OK
	OK
	Yes

	5
	2004.09.20
	OK
	OK
	OK
	Yes

	6
	2004.09.20
	OK
	OK
	OK
	Yes

	7
	2004.09.20
	OK
	OK
	OK
	Yes


Conclusion:

The valves pass the drop test.

3.2.  Initial tightness testing 

The following assemblies were tested
· AAV 2004/36/003-1,2,3 and 7 with their connector on a PVC-pipe DN 32; the pipe being inside the AAV-connector

· AAV 2004/36/003- 1,2 and 3 with their connector in a PVC-pipe DN 40; the pipe being also inside the AAV-connector 

· AAV 2004/36/003- 4 5 and 6 without connector glued in PVC coupling, which on its turn was glued on a PVC-pipe DN 50.
· AAV 2004/36/003-1,2 and 3 without connector in a PVC coupling, with rubber ring on both sides, on a PVC-pipe DN 50 mm.

Results:

	AAV with connector on a PVC-pipe DN 32; the pipe being inside the AAV-connector
	Date : 2004/09/20

	AAV

sample n°

2004/36/003-
	30 Pa level
	500 Pa level
	10000 Pa level
	30 Pa level

2nd attempt (1)
	Pass

(2)

	
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	

	1
	34
	32
	500
	485
	10000
	9840
	/
	/
	Y

	2
	35
	35
	500
	490
	10000
	9600
	/
	/
	Y

	3
	35
	34
	500
	500
	10000
	9820
	/
	/
	Y

	7
	36
	36
	500
	485
	10000
	9820
	/
	/
	Y

	(1) : due to the manipulation during the mounting of the valve, the first low pressure test can be negative; in case a second low pressure test, after the high pressure test, is OK, then BBRI considers the AAV as tight.

(2) : Y= does pass the test;  N= does not pass the test


	AAV with connector in a PVC-pipe DN 40; the pipe being inside the AAV-connector
	Date : 2004/09/20

	AAV

sample n°

2004/36/003-
	30 Pa level
	500 Pa level
	10000 Pa level
	30 Pa level

2nd attempt(1)
	Pass

(2)

	
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	

	1
	36
	34
	500
	490
	10000
	9920
	/
	/
	Y

	2
	35
	35
	500
	490
	10000
	9900
	/
	/
	Y

	3
	34
	33
	505
	495
	10000
	9880
	/
	/
	Y

	(1): due to the manipulation during the mounting of the valve, the first low pressure test can be negative; in case a second low pressure test, after the high pressure test, is OK, then BBRI considers the AAV as tight.

(2) : Y= does pass the test;  N= does not pass the test


	AAV glued in a coupling on a PVC- pipe DN50
	Date : 2004/09/21

	AAV sample n°

2004/36/003-
	30 Pa level
	500 Pa level
	10000 Pa level
	30 Pa level

2nd attempt(1)
	Pass

(2)

	
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	

	4
	34
	36
	500
	495
	10000
	9940
	/
	/
	Y

	5
	35
	34
	500
	495
	10000
	9920
	/
	/
	Y

	6
	36
	40
	505
	495
	10000
	9900
	/
	/
	Y

	(1): due to the manipulation during the mounting of the valve, the first low pressure test can be negative; in case a second low pressure test, after the high pressure test, is OK, then BBRI considers the AAV as tight.

(2) : Y= does pass the test;  N= does not pass the test


	AAV in a coupling with rubber ring on a PVC- pipe DN50
	Date : 2004/09/21

	AAV sample n°

2004/36/003
	30 Pa level
	500 Pa level
	10000 Pa level
	30 Pa level

2nd attempt(1)
	Pass

(2)

	
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	

	1
	34
	33
	510
	490
	10000
	9880
	/
	/
	Y

	2
	35
	33
	500
	490
	10000
	9860
	/
	/
	Y

	3
	35
	34
	505
	495
	10000
	9840
	/
	/
	Y

	(1): due to the manipulation during the mounting of the valve, the first low pressure test can be negative; in case a second low pressure test, after the high pressure test, is OK, then BBRI considers the AAV as tight.

(2) : Y= does pass the test;  N= does not pass the test


Conclusion:

The AAV pass the test for all tested assemblies.

3.3.  Tightness testing after endurance of the AAV 

The endurance cycles comprised: 

· 16 hours of cycles at 20°C, 

· followed by 8 hours of cycles at 60°C 

The following assemblies were submitted to an endurance cycling:

· AAV 2004/36/003- 7 with connector on a PVC-pipe DN32; tested on 2004/09/22 at 20°C and on 2004/09/24 at 60°C
· AAV 2004/36/003- 5 without its connector glued in a PVC- coupling DN50; tested on 2004/09/22 at 20°C and on 2004/09/24 at 60°C.
· AAV 2004/36/003- 3 without its connector in a PVC-coupling DN 50 with rubber ring; tested on 2004/09/23 at 20°C and on 2004/09/28 at 60°C
· AAV 2004/36/003-2 with its connector in a PVC-pipe DN40; tested on 2004/09/23 at 20°C and on 2004/09/28 at 60°C.
After both series of cycles at a given temperature, the tightness of the assembly was verified by testing the aged assembly.

Results:
	Tightness test after endurance at 20°C:
	

	AAV sample n°

2004/36/003-
	30 Pa level
	500 Pa level
	10000 Pa level
	30 Pa level

2nd attempt(1)
	Pass

(2)

	
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	

	7
	36
	36
	495
	500
	10000
	9900
	/
	/
	Y

	5
	36
	34
	500
	500
	10000
	9880
	/
	/
	Y

	3
	36
	34
	500
	495
	10000
	9710
	/
	/
	Y

	2
	35
	32
	500
	480
	10000
	9890
	/
	/
	Y

	(1): due to the manipulation during the mounting of the valve, the first low pressure test can be negative; in case a second low pressure test, after the high pressure test, is OK, then BBRI considers the AAV as tight.

(2) : Y= does pass the test;  N= does not pass the test




	Tightness test after endurance at 60°C:
	

	AAV sample n°

2004/36/003-
	30 Pa level
	500 Pa level
	10000 Pa level
	30 Pa level

2nd attempt(1)
	Pass

(2)

	
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	Pressure at start

(Pa)
	Pressure after 5 minutes (Pa)
	

	7
	35
	0
	500
	490
	10000
	9780
	36
	40
	Y

	5
	35
	35
	500
	495
	10000
	9920
	/
	/
	Y

	3
	36
	34
	500
	485
	10000
	9840
	/
	/
	Y

	2
	34
	0
	500
	490
	10000
	9860
	35
	38
	Y

	(1): due to the manipulation during the mounting of the valve, the first low pressure test can be negative; in case a second low pressure test, after the high pressure test, is OK, then BBRI considers the AAV as tight.

(3) : Y= does pass the test;  N= does not pass the test




Conclusions:

The AAV pass the test for all tested assemblies.

3.4. Opening characteristic and airflow capacity

These measurements were done on 2004/09/28, in the following environmental conditions:

· atmospheric pressure: 
1019 mbar

· air temperature 

23.5°C

· relative humidity: 

60%

Results:

	assembly
	AAV sample n°

2004/36/002-
	Opening pressure

(Pa)
	Air capacity:
airflow at

–250 Pa

(l/s)
	Airflow at

–150 Pa

(l/s)

	DN 32
	7
	-88
	5.81
	4.33

	
	2
	_75
	5.96
	4.46

	
	3
	-94
	5.93
	4.42

	DN 40
	7
	-91
	7.25
	5.26

	
	2
	-63
	7.72
	5.55

	
	3
	-99
	7.30
	5.26

	DN 50 with rubber ring
	7
	-92
	7.19
	5.13

	
	2
	-86
	7.42
	5.26

	
	3
	-95
	7.22
	5.18

	DN 50 glued
	4
	-84
	7.58
	5.49

	
	5
	-95
	7.45
	5.29

	
	6
	-85
	7.37
	5.24


Remarks:

1. The air capacity was measured at -250 Pa. The standard allows however to do this measurement from -240 to -260 Pa. The air capacity at -240 or -260 Pa can be calculated from the ones measured above, by multiplying them by 0.98 (= SQRT 240/250) or 1.02 (=SQRT 260/250) respectively.


2. The above tabulated flow rates (q meas) can be converted to standard conditions (20°C and 101325 Pa) by applying the following formula :
q cor = q meas *(293/(273 +23.5))* (101900/101325)= 0.994 q meas 
The standard does however not require such a correction.
Conclusions:

· The opening pressure is between 0 and -150, the valves pass the test.

· The air capacity at 23.5°C, is depending upon the type of assembly:


	Assembly
	When measured at :

	
	-240 Pa
	-250 Pa
	-260 Pa

	DN 32
	5.64 l/s
	5.81 l/s
	5.93 l/s

	DN 40
	7.10 l/s
	7.25 l/s
	7.39 l/s

	DN 50 –rubber ring 
	7.05 l/s
	7.19 l/s
	7.33 l/s

	DN 50 -glued
	7.22 l/s
	7.37 l/s
	7.52 l/s


· There is a measurable flow at -150 Pa, the valves pass the test.

3.5. Effectiveness at temperatures below zero
This test was done on the AAV 2004/35/003 - 1, with an insulation cap on its top, installed on a  DN32.

Results: 

	Date
	Hour
	Air flow capacity 

at –250 Pa

(l/s)
	Temperature in the cool box

(°C)
	Comment

	2004/10/04
	08.00
	5.26
	22
	

	2004/10/05
	08.30
	/
	-20
	Discharge of water at +40°C at 10 l/min for 5 minutes

	
	09.30
	5.1
	-20
	Residual water height in trap: 36 mm


Conclusion:

The AAV can be considered as effective at temperatures below zero, as the second air flow is not less than 90% of the first value and the water level in the trap is >25 mm.

4. General conclusion

For the assemblies tested, the STUDOR MINI-VENT valves can be considered as AI valves according to  EN 12380 of December 2002.

Photos

	[image: image2.png]





	Photo 1: package of the MINI-VENT


	[image: image10.png]


[image: image3.png]





	Photo 2 : AAV with connector


	[image: image4.png]




	Photo 3 : AAV without connector


	[image: image5.png]





	Photo 4:AAV top view with markings


	[image: image6.png]




	Photo 5: AAV without connector, view from downside


	[image: image7.png]



	[image: image8.png]




	Photo 6: dismantled AAV - left :view on AAV with removed top; right:membrane


	[image: image9.png]





	Photo 7: connector


	
	

	Photo 8: AAV glued in coupling DN 50 
	Photo 9 : coupling with rubber ring


Identification of the measuring equipment:

	Test
	Measurement
	Equipment

	Tightness of AAV
	Low pressure
	Inclined manometer 0 -12 mm water

	
	Medium pressure
	Inclined manometer 0-100 mm water

	
	High pressure
	U-tube manometer 0- 1500 mm water

	Endurance
	Pressure cycling 
	Electric (diaphragm) pressure transducer 0 – 2.5 mbar

	
	Temperature in the box
	Thermocouple

	Opening characteristics and air capacity
	pressure,
	Inclined manometer 0-100 mm water

	
	Air flow
	Orifice flow metering connected to an inductive pressure pick-up 0-1000Pa

	Effectiveness at low temperature
	Temperature in the box
	Thermocouple 

	
	pressure
	Inclined manometer 0-100 mm water

	
	Air flow
	Orifice flow metering connected to an inductive pressure pick-up 0-1000Pa





23 mm





69 mm





66.4 mm









